## Revive mixed lube -monthly suit
Gas turbine lube oil analysis program
Lube oil specification: "Q8 VOLTA EP-32" comingled with 10% "EcoSafe Revive" fluid No. of samples to be analysed per month: 2 No. Total No. of samples from August 2021 to April 2022: 18 No. Contractor scope: supply of new sample bottles (500 ml capacity), packing & shipping to laboratory, oil analysis & providing results
Monthly analysis to be carried out
Sl.No. | Description of the test | Standard / Test method
1 | Colour/Appearance | ASTM D1500
2 | Kinematic Viscosity at 40 degC | ASTM D445
3 | Water content by Karl Fischer method | ASTM E203 (or) ASTM D6304
4 | Total Acid Number (TAN) | ASTM D664 (or) ASTM D974
5 | Cleanliness by "Poreblock method" | ISO 4406 / ASTM D5452
6 | Inductively Coupled Plasma Atomic Emission Spectrometry (ICP) | ASTM D5185
7 | Infrared Spectrometry (FT-IR) | ASTM D2412
8 | Varnish Potential (MPC) | Modified ASTM D7843 * Please refer to the note
* Note: 1. Varnish Potential of PAG oil cannot be accurately determined by MPC using a petroleum solvent 2. An equivalent percentage of petroleum solvent and isopropyl alcohol should be used for systems containing PAG oil chemistry. 3. The modified procedure adds isopropyl alcohol should be rounded to the nearest 5% using the following formulas: IPA % of MPC solvent for ISO 32 = 728 * ρsample @ 15 °C (g/cm3) – 626 IPA % of MPC solvent for ISO 46 = 743 * ρsample @ 15 °C (g/cm3) – 643 IPA % of MPC solvent for ISO 68 = 781 * ρsample @ 15 °C (g/cm3) – 684 4. The filter must be quickly preserved with a petroleum solvent. MPCIPA Normal ΔE <30, Critical = >30.